## Fittings_General_Information
ID | Fitting name | Brand | Model | Type of fittings | Materials | Nominal diameter | Pressure class (PN) | Manufacturer | Sealing method | Connection types | Surface coating | Operating temperature | Operating pressure (bar) | Inspection/replacement frequency | Common problems encountered | Average lifespan in operation | Replacement method/frequency | Environmental conditions affecting performance | H2 ready according to manufacture | TSO/DSO
1 | 002ETETRF | Biagini Piero and others | 3D | elbows, tees, reducers, couplings, flanges | Carbon steel | 15-600 DN | Underground | Biagini Piero and others | welding | Welded | external | +5°C÷+25°C | 0,02÷5 bar | 3 year (inspection) | welding failure | 60 years | on demand | moisture levels | TRUE | DSO
2 | 002ETETRF | Biagini Piero and others | 3D | elbows, tees, reducers, couplings, flanges | Carbon steel | 15-600 DN | Overground | Biagini Piero and others | welding | Welded | external | -10°C÷+55°C | 0,02÷5 bar | 3 year (inspection) | welding failure | 60 years | on demand | moisture levels | TRUE | DSO
3 | 002ETETRF | Eurostandard and others | 3D | elbows, tees, reducers, couplings | Polyethylene | 15-600 DN | Underground | Eurostandard and others | welding | Welded | none | +5°C÷+25°C | 0,02÷5 bar | 3 year (inspection) | pipe or welding failure | 60 years | on demand | temperature and others | TRUE | DSO
4 | 002ETF | Biagini Piero and others | EN 1092-1 | flanges PN 10÷25 | Carbon steel | 25-600 DN | Overground | Biagini Piero and others | welding | Welded | none | -10°C÷+55°C | 0,02÷25 bar | 3 year (inspection) | leakage | 60 years | on demand | temperature and others | TRUE | DSO
5 | 002ETF | Biagini Piero and others | asme B16.5 ANSI 600 | flanges ANSI B16.5 (ANSI 600) | Carbon steel | 25-250 DN | Overground | Biagini Piero and others | welding | Welded | none | -10°C÷+55°C | ANSI 600 (~100 bar) | 3 year (inspection) | leakage | 5 years | regular schedule | temperature and others | TRUE | DSO
6 | 001SAERC | Several brands | ASME B16.9 | elbows, tees, reducers, couplings, flanges | Carbon steel | 60 -1050 DN | Underground | Several | welding | Welded | external | -29°C÷+100°C | 0÷300 bar | yearly | leakage occasionaly | 60 years | on demand | Not relevant | TRUE | TSO
7 | 001SAERC | Several brands | ASME B16.11 | elbows, tees, reducers, couplings, flanges | Carbon steel | 15-40 DN | Underground | Several | welding | Welded | external | -29°C÷+100°C | 0÷300 bar | yearly | leakage occasionaly | 60 years | on demand | Not relevant | TRUE | TSO
8 | 001SAERC | Several brands | ASME B16.9 | elbows, tees, reducers, couplings, flanges | Carbon steel | 60 -1050 DN | Overground | Several | welding | Welded | external | -29°C÷+100°C | 0÷300 bar | yearly | leakage occasionaly | 60 years | on demand | Not relevant | TRUE | TSO
9 | 001SAERC | Several brands | ASME B16.11 | elbows, tees, reducers, couplings, flanges | Carbon steel | 15-40 DN | Overground | Several | welding | Welded | external | -29°C÷+100°C | 0÷300 bar | yearly | leakage occasionaly | 60 years | on demand | Not relevant | TRUE | TSO
10 | 002MAETR | IRC SPA |  | elbows, tees, reducers | Carbon steel | DN 15÷900 | PN 100 | IRC SPA |  | welded or flanged | internal & external | -10°C÷+60°C | 0,5÷75 bar |  |  |  | on demand |  | TRUE | TSO
11 | 002MAETR | INDUSTRIA MECCANICA BASSI LUIGI & C |  | elbows, tees, reducers | Carbon steel | DN 125÷1400 | PN 100 | INDUSTRIA MECCANICA BASSI LUIGI & C |  | welded or flanged | internal & external | -10°C÷+60°C | 0,5÷75 bar |  |  |  | on demand | moisture levels | TRUE | TSO
12 | 002MAETR | TECTUBI RACCORDI S.P.A. |  | elbows, tees, reducers | Carbon steel | DN 15÷1400 | PN 100 | TECTUBI RACCORDI S.P.A. |  | welded or flanged | internal & external | -10°C÷+60°C | 0,5÷75 bar |  |  |  | on demand | temperature and others | TRUE | TSO
13 | 002MAETR | RACCORDI FORGIATI SRL |  | elbows, tees, reducers | Carbon steel | DN 15÷600 | PN 100 | RACCORDI FORGIATI SRL |  | welded or flanged | internal & external | -10°C÷+60°C | 0,5÷75 bar |  |  |  | on demand | temperature and others | TRUE | TSO
14 | 002MAETR | VALVITALIA S.P.A. |  | elbows, tees, reducers | Carbon steel | DN 15÷1400 | PN 100 | VALVITALIA S.P.A. |  | welded or flanged | internal & external | -10°C÷+60°C | 0,5÷75 bar |  |  |  | on demand | temperature and others | TRUE | TSO
15 | 002MAETR | GALPERTI SRL |  | elbows, tees, reducers | Carbon steel | DN 15÷1200 | PN 20 ÷ PN 100 | GALPERTI SRL |  | flanged | internal & external | -10°C÷+60°C | 0,5÷75 bar |  |  |  | on demand |  | TRUE | TSO
16 | 002MAETR | OFFICINE AMBROGIO MELESI & CO. SRL |  | elbows, tees, reducers | Carbon steel | DN 15÷1200 | PN 20 ÷ PN 100 | OFFICINE AMBROGIO MELESI & CO. SRL |  | flanged | internal & external | -10°C÷+60°C | 0,5÷75 bar |  |  |  | on demand |  | TRUE | TSO
17 | 004MEFF |  | Welded TOR's fittings | fitting | Carbon steel, mainly P355 (A516) | DN 50 (2") | Underground |  | o-ring | Welded | External acc. EN 10290 | -29 to +60 C | 84 bar | No replacement | Smal leakage possibility | Not defined | on demand | The same as the gas pipeline | FALSE | TSO
18 | 004MEFF |  | Branch connection fittings with reinforcement | fitting | Carbon steel, mainly P355 (A516) | DN 50 up to DN 1000 | Underground |  | flange - gasket | Welded | External acc. EN 10290 | -29 to +60 C | 84 bar | No replacement | Elements welded to the gas pipeline | Not defined | on demand | The same as the gas pipeline | FALSE | TSO
19 | 004MEFF |  | Reduced branch connection fittings with reinforcement | fitting | Carbon steel, mainly P355 (A516) | DN 50 up to DN 1000 | Underground |  | flange - gasket | Welded | External acc. EN 10290 | -29 to +60 C | 84 bar | No replacement | Elements welded to the gas pipeline | Not defined | on demand | The same as the gas pipeline | FALSE | TSO
20 | 004MEFF |  | Branch fittings with reinforcement | fitting | Carbon steel, mainly P355 (A516) | DN 50 up to DN 1000 | Underground |  | flange - gasket | Welded | External acc. EN 10290 | -29 to +60 C | 84 bar | No replacement | Elements welded to the gas pipeline | Not defined | on demand | The same as the gas pipeline | FALSE | TSO
21 | 004MEFF |  | Split tee fittings | fitting | Carbon steel, mainly P355 (A516) | DN 50 up to DN 1000 | Underground |  | flange - gasket | Welded | External acc. EN 10290 | -29 to +60 C | 84 bar | No replacement | Elements welded to the gas pipeline | Not defined | on demand | The same as the gas pipeline | FALSE | TSO
22 | 004MEFF |  | Flange connections acco to. EN 1094 (PN designations) | flanges | Carbon steel, mainly P355 (A516) | DN 15 up. to DN 1000 | Overground |  | flange - gasket | Flanged | External | -29 to +60 C | 85 bar | No replacement | Elements welded to the gas pipeline | Not defined | on demand | The same as the gas pipeline | FALSE | TSO
23 | 004MEFF |  | Flange connections acco to. EN 1759 (Class designations) | flanges | Carbon steel, mainly P355 (A516) | DN 15 up. to DN 1000 | Overground |  | flange - gasket | Flanged | External | -29 to +60 C | 85 bar | No replacement | Elements welded to the gas pipeline | Not defined | on demand | The same as the gas pipeline | FALSE | TSO
24 | 003OCERT |  | ASME B16.9 | elbows, reducers, tees | A403 WP316-S, A403 WP316-W, A182 F316, A479 316 | 15-60 DN | PN 3000, 6000,9000 |  | welding | Welded |  | -50°C÷+100°C | [6 empty] | FALSE | TSO